City of Tracy

333 Civic Center Plaza

Tracy, CA 95376

DEVELOPMENT SERVICES DEPARTMENT

MAIN   209.831.6400

FAX     209.831.6439

www.cityoftracy.org

October 31, 2019

Application Number: 19-0881/19-0949

Dear Applicant,

The Building Safety Division has completed the plan review based on the current edition of California Building Codes and all applicable City of Tracy Municipal Ordinances.

At this time, the project cannot be approved as submitted.  The corrections are attached to this letter.

The Building Safety Division’s policy is to perform a comprehensive review during the first submittal.  Thus, if an item is missed on the first round of review which does not result in a fire, life safety or accessibility matter, the staff reviewer will not include that as a new correction but will inform the applicant of the deficiency and redline the requirement on the approved set of plans for construction.  However, in cases where submitted plans contain a significant amount of code violations, inconsistent or missing information and/or details, it becomes impractical to perform a fully comprehensive review based on the incomplete submittal.  Thus, in these cases, additional comments may be added during the subsequent rounds of plan review until the project submittal documents are complete and ready for construction as required by the California Building Code.

When addressing the comments of revised plans, submit a written response to each comment. Indicate which details, specifications, and/or calculations show the requested correction by clouding all revisions and show revised delta designation for all changes. Using complete and clear responses will expedite the re-check and approval of the project. Identify the revisions in the revision box with a corresponding date and type of correction.

If any changes have been made to the plan documents unrelated to those items identified in the comment lists, please list the changes on a separate sheet and include in your submittal documentation.

Provide three (3) complete sets of revised plans and two (2) sets of revised calculations and/or specifications. Plans and documents must be wet stamped and signed by the Architect and/or Engineer of Record.  Return Plans and documents to City of Tracy Development Services, 333 Civic Center Plaza Tracy, CA 95376.

Re-submittals that do not include the complete plan review correction list with responses, complete plans and supporting documents (i.e. structural calculations, energy forms, etc.) will delay the process.

Should you have any questions regarding this procedure, please contact the City of Tracy Permit Center at (209) 831-6400.

Thank you,

City of Tracy Plan Review Team

PROJECT INFORMATION

APPLICATION NUMBER:	19-0881/19-0949, Submittal #3

PROPERTY ADDRESS:	41 W Highland

SCOPE OF WORK:		REVISED SCOPE OF WORK REQUIRED

1 – Remodeling of an existing dwelling

2 – Additions of 239 sq ft to the existing 1st floor

3 – Addition of new 2nd floor with an area of 1735

4 – Retrofit of Existing Foundation

5 – Demolition of the existing roof to be replaced with new roof

6 – Renovation and Remodeling the Exterior Elevations

7 – New Plumbing & Electro-mechanical works to supersede the existing

8 – Install new windows & doors to supersede the existing

9 – Adding new ADU with floor area 1200 SF

PROPERTY OWNER:  	Joan Evans

ENGINEER: 			Amana Engineering & Construction

CONTACT INFO: 		(510) 715-2666 // amanaeng@gmail.com

PLANS EXAMINER:  	Chrystle Takehara

CONTACT INFO:		(209) 831-6486 // chrystle.takehara@cityoftracy.org

PLAN CHECK ENGINEER:  	Sean McNamara

CONTACT INFO:		(209) 831-6400 // sean.mcnamara@cityoftracy.org

PROJECT DATA

OCCUPANCY GROUP(S): 		R-3, U

TYPE OF CONSTURCTION: 	V-B

NUMBER OF STORIES: 		2

CONDITIONED FLOOR AREA: 	SFD:		1st Floor: 1848 SF

2nd Floor: 1735 SF

Garage:	6 car garage 2 car garage

ADU: 		1200 SF

UNCONDITIONED FLOOR AREA: 	1030 SF

FIRE SPRINKLER SYSTEM: 	No

VALUATION:

PLAN REVIEW COMMENTS

Plan review comments are listed on the following pages.  Please review and respond accordingly.

Note that outstanding items in need of attention are indicated in Red, Bold, and Italics.

PLAN REVIEW COMMENTS

GENERAL

- Our records indicate that this property is related to Code Enforcement Case 19CD-0766.  Note the following violations indicated in the code case:

    - Missing Roof, Covered with black tarps, Outhouse in front

PC2. Comment informational.  No further comment.

- Our records indicate that this property is related to Code Enforcement Case 19CD-0924.  Note the following violations indicated in the code case:

    - An inspection was done per a request from TFD for hazards in a partially demolished residence associated with a structure fire at 1105 hrs

    - The remnants of a fire on the north wall of the living room was noted.

    - All of the interior wall coverings, ceiling coverings, attic space floor sheathing and the roof were noted removed.

    - Evidence of the structure being occupied including a refrigerator, cooking appliance, food, a couch and chair were observed in the area of origin where the fire damaged wood studs and floor were located.

    - A tub of soapy water and dishes, a hose was observed in the back yard.

    - Portions of the brick foundation at the north side of the residence were noted missing or damaged.

    - The tank less water heater at the east side of the residence was noted damaged.

    - Due to the exposed wiring, compromised roof and wall structure, damaged water heater and evidence of the structure being occupied after the contractor was previously directed to vacate and stop work(with a Red Tag issued). P.G.& E.  was contacted and directed to remove the electric service and the gas meters.

PC2. Comment informational.  No further comment.

- The demolition of the residence occurred prior to the issuance of a permit.  At the time of inspection, the applicant may be required by the building inspector to remove a portion (or portions) of unpermitted construction to verify proper installation of construction practices.  Neither the building official nor the City of Tracy shall be liable for any expense entailed in the removal or replacement of any material required to allow for inspection.

PC2. Comment informational.  No further comment.

- Indicate if there will be a 2nd address for the accessory dwelling unit.  To obtain a secondary address for this unit, contact Anju Pillai at 209.831.6455.  Address must be approved prior to issuance of permit.  Building address numbers to be a minimum of 4 inches high on a contrasting background and placed in a position that is plainly visible from the street fronting the property as per CRC R319.1

PC2.  Applicant to clarify if accessory dwelling unit will have a separate address.

PC3. No further comment

- Applicant to obtain demolition permit, including approval from the San Joaquin County Air Pollution Control District for proposed demolition.

PC3.  Comment informational.  No further comment.

ARCHITECTURAL

Sheet A.02

- The site plan indicates a setback of 3 feet from the property line.  The addition to the garages and existing dwelling is still proposed to be 3 feet from the property line and the new accessory dwelling unit is proposed to be 4 feet from the property line on both the east and west sides of the property.  Since the structures are not protected with an automatic fire sprinkler system, the applicant must meet requirements of CRC Table R302.1(1) for fire resistance of walls, projections, and openings.

PC2. Indicate where the 1 hour minimum fire-resistance rating is indicated on plans on sheet A.02. The accessory dwelling, garage, and addition to the existing dwelling have to meet the requirements of CRC Table R302.1(1).  This includes 1 hour rating of the walls with less than 5 feet of minimum fire separation distance, 1 hour fire resistance rating on the underside of the projections, and protected penetrations.

PC3.

- Identify the method and provided locations for the 1 hour fire resistance rating on the underside of projections located <5’ to the adjacent property line, or provide details to demonstrate the exceptions found in the footnotes of table R302.1(1) will be met.

- The south wall of the detached garage is noted as being rated, however the west wall is required to be provided with the rating based on the location <5’ to the west side property line please revise accordingly.

- Indicate on the site plan the proposed location, connection, length, size, type, and method of running utilities (sewer, water, gas, electric, etc.) to the 6 car garage and accessory dwelling unit.

PC2.  Provide the following:

  - Confirm that the capacity of the gas meter at the existing dwelling is able to supply the new demand from the Accessory dwelling unit.

  - Provide gas line isometric for main dwelling and accessory structure.

  - Indicate size of new electrical panel for ADU. Clarify if the new accessory dwelling unit is receiving a new service for the ADU or if the electrical at the ADU is connected to the main panel.

  - New sanitary sewer for ADU indicates that it will be run to an existing Sanitary Sewer Clean out.  Applicant to indicate if existing connection from Sanitary Sewer Clean out to main connection is sized for total from Existing Dwelling, New 2-car garage, and New ADU.

  - Clarify if there will be a subpanel for the 2 car carport/garage. Floorplan for carport/garage indicates a sub-panel.  Indicate size and provide electrical load calculations.

  - Clarify why there is a water line and waste line being installed to the carport/garage on sheet A.02.  Is there a proposed water fixture?

PC3. No further comment.

Sheet A.04

- Revise calculations for ADU and Accessory Dwelling Unit roof ventilation, providing the manufacturer’s net free vent area of the vents.  Note that for gable louvered vents and soffit vents, the product does not provide the same net free vent area as the size of the vent.  The manufacturer provides the net free area of venting for their product.  Use this net free area of venting value in calculating the required vent area.  For example, A 12 x 14 louvered vent on the Home Depot Website indicates a net free area of 65 sq. in.

PC2. Because the ADU and existing dwelling are within 5 feet of the property line, this limits the location of soffit vents.  Since the roof projections are within 2 to 5 feet of the property line, they need to be 1 hour fire resistance rated on the underside.  However, sheet A.04 indicates that there will be continuous soffit vents at this location.  Clarify and revise.

PC3. Revised ventilation calculations are acceptable however rating of projections or compliance with exceptions found in footnotes of table R302.1(1) is still required.

- Indicate how access to the addition area is provided as per CRC R807.1.

PC2. Applicant to indicate on sheet A.04, which areas of the existing dwelling roof are new and which are existing.  Applicant to provide access between new and existing areas or provide separate attic access in new roof areas.

PC3. Revised scope of work required to clearly identify main dwelling being demolished and reconstructed from the foundation up based on PC2 structural response. Please also see PC3 comment for comment 67.

Sheet A.05

- Identify location of Egress windows and proposed tempered glazing.

PC2. No further comment.

- Indicate that the floor or landing at exterior doors shall have a dimension of not less than 36 inches measured in the direction of travel the landing shall be not more than 7 ¾ inches below the top of the threshold, and with a slope not to excel ¼ unit vertical in 12 units horizontal as per CRC R311.3.

PC2. No further comment.

- Provide smoke alarm outside each sleeping area as per CRC R314.3.  Currently there only smoke alarms within the rooms.

PC2. No further comment.

- Provide additional carbon monoxide alarm outside of Bedroom #4 as per CRC 315.3 which requires a carbon monoxide alarm outside each separate sleeping area in the immediate vicinity of the bedrooms.  With the location of the gas water heater across the hall from Bedroom #4, it is important to include this safety device.

PC2. No further comment.

- Revise calculations for crawl space to include the net free vent area.  Also indicate if the new addition area will cover existing vents and if the area will be connected in the crawl space.

PC2. No further comment.

GENERAL NOTES ON ALL FLOOR PLANS

- Electrical Note b indicates 2 dedicated circuits for appliances per CEC 210.52(C)(3). This section is for peninsular countertop spaces receptacle outlet.  Provide correct Section.

PC2. No further comment.

- Electrical Note d indicates section 206.9, which does not exist in the CEC.  Revise.

PC2. No further comment.

- Electrical Note g references the “DCMC”.  The City of Tracy uses the City of Tracy Municipal Code and not DCMC.  Clarify.

PC2. No further comment.

- General Notes 3 indicates attic access as per CRC R806.1.  Section R806.1 refers to roof ventilation. Attic Access is per CRC R807.1.

PC2. No further comment.

- Plumbing note 8 indicates that per CPC 411.10, control valves and shower heads shall be located on the sidewall of shower compartments.  However section 411.10 does not exist.  Section 411 is for water closets.

PC2. No further comment.

- Plumbing note 15 indicates that excess gas shut-off devices as per C.C.Co.  Clarify.

PC2.  No further comment.

- Note for “26 duct gauge rigid ducted range hood references CBC 1203.4.2.1.” Revise for CRC or CMC reference since project is under CRC

PC2. No further comment.

- Note under electrical panel legend indicates that for “exterior lighting, luminaires to be high efficiency or have all the following controls per CEC 150.0(k)(9A).”  This section does not exist.  Residential outdoor lighting are to meet requirements of CEnC 150.0(k)3.

PC2. No further comment.

- Notes under electrical plan legend indicate that “all new recessed lighting fixtures installed in insulated ceilings shall be IC (insulation cover) and AT (air tight) rated, and shall be sealed between the fixture housing and the gyp board with a gasket or cault per CNC 150(k)12.  Recessed downlight luminaires in ceilings are to comply with CEnC 150.0(k)1.C.

PC2. No further comment.

- Notes under electrical plan legend reference the CBC in multiple areas.  Note that project falls under the jurisdiction of the CRC and not CBC.  Revise note references to CBC.

PC2. No further comment.

- Notes under Electrical notes that “All GFCI Protected receptacles shall also be provided with tamper resistant feature” references CEC 210.8(A)(6).  However, this section refers to GFCI protection in Kitchens.  Provide correct reference.

PC2. No further comment.

- Notes that “smoke and carbon monoxide alarms shall receive their primary power from the building’s electrical system and shall have a battery backup power supply” reference CBC 907.2.11.6 and CBC 915.4.1.  Use CRC reference for R314.6 for Smoke Alarms and R315.5 for Carbon Monoxide Alarms.

PC2. No further comment.

Sheet A.06

- Based on floor plan of first and second floor, it appears that the addition for the existing dwelling creates a 2-family dwelling.  Indicate if this is the case.  If so, provide a minimum 1-hour fire resistance rating as per CRC R302.3.  Details on Sheet A.12 also support that there will be fire assemblies between the 2-dwellings.  Clarify on floor plan where these details will be used.

PC2. No further comment.

- Based on floor plan of first and second floor, it appears that the addition for the existing dwelling creates a 2-family dwelling.  For the floor-ceiling assemblies separating the dwelling units, provide air-borne and impact sound insulation as per CRC Appendix K.  Details on Sheet A.12 also indicate that there will be the sound insulation the 2-dwellings.  Clarify on floor plan where these details will be used.

PC2. No further comment.

- Provide smoke alarm outside each sleeping area as per CRC R314.3.  Currently there only smoke alarms within the rooms.

PC2. No further comment.

- Provide Carbon monoxide alarm outside each separate sleeping area in the immediate vicinity of the bedrooms per CRC R315.3.  Currently, there is not a carbon monoxide alarm outside bedroom 3 and 4.  With proximity of gas appliances from the water heater and clothes dryer, it is important to provide carbon monoxide alarm.

PC2. No further comment.

- Identify locations of Emergency Egress Windows Windows and proposed tempered glazing.

PC2. No further comment.

- The stairway indicates that there are (2) 2640 hung up windows located at the stairs.  Per CRC R308.4.6, glazing adjacent to stairs and ramps where the bottom exposed edge of the glazing is less than 36 inches above the plane of the adjacent walking surface, landings between flights of stairs and ramps shall be considered to be a hazardous location.  Indicate if these windows will be tempered glazing as per R308.3.

PC2. No further comment.

- Stairway has callout, which indicates “For staircase details, see sheet A.12, typ.”  Note that Stairway details are provided on sheet A.13 and not A.12.

PC2. No further comment.

Sheet A.07

- Windows on 1st and 2nd floor plans on the western wall indicate a 6040, 5040, and 6040 windows.  However, the western elevation indicates that there are 2 single hung windows for each location.  The window openings also show that the windows slide into each other.  Clarify window type on elevation and floor plans. Demonstrate that window types will be able to meet emergency escape opening requirements.

PC2. No further comment.

- Windows on 1st and 2nd floor plan on the southern wall indicate (2) 6068 sliding glass doors to the porch on the 1st floor and (2) 6040 sliding windows and (1) sliding glass door to the balcony on the 2nd floor.  However, on southern elevation, the sliding glass doors look like sliding glass windows.  Clarify on elevation if these are proposed sliding glass doors or sliding glass windows.  Elevation also demonstrates that there are 2 single hung windows to make the 6040 windows.  Clarify window type on elevation and floor plans. Demonstrate that window types will be able to meet emergency escape opening requirements.

PC2. No further comment.

- Indicate if proposed exterior wall covering of stucco is 3-coat stucco, or provide manufacturer’s specification, installation requirements, and approved listing number for proposed 1-coat or 2-coat stucco.

PC2. No further comment.

Sheet A.08

- Clarify window sizes and types with proposed on 1st and 2nd floor plans.

PC2. No further comment.

Sheet A.09

- Energy forms indicate that there is 50 gal gas water heater provided for the ADU.  Indicate location on floor plan.

PC2. No further comment.

- Energy forms indicate a Split Air Conditioner unit.  Indicate location on plans.

PC2. No further comment.

- Energy forms indicate an IAQ fan.  Indicate location.

PC2. No further comment.

Sheet A.11

- Indicate that the garage slab will be sloped to a drain or toward the main vehicle entry doorway as per CRC R309.1.

PC2. No further comment.

Sheet A.12

- Details indicate that there are proposed 1-hour fire rated wall assemblies and sound rated floor assemblies.  Indicate on the floor plan where these are proposed to be constructed.

PC2. Applicant to still indicate areas that are 1-hour fire rated due to proximity to property lines as per CRC Table R302.1(1).

PC3. 1-hour wall assembly has been shown at the south detached garage wall, however the west wall requires rating based on its fire separation distance.

- List fireblocking requirements per CRC R302.11.

PC2. No further comment.

- List draftstopping requirements per CRC 302.12.

PC2. No further comment.

Sheet A.13

- Provide a detail showing actual size of handrail profile with the following dimensions:

  - The finger recess shall begin within a distance of 3/4" measured vertically from the tallest portion of the profile.

  - The finger recess shall achieve a depth of not less than 5/16” within 7/8” below the widest portion of the profile.

  - The depth shall continue for not less than 1-3/4" below the tallest portion of the profile.

  - The width of the handrail above the recess shall be not less than 1-1/4” and not more than 2-3/4”.

  - Edges shall have a radius of not less than 0.01”.

**Note: This can be a deferred submittal.  If including as a deferred submittal, notate “Handrail detail is a deferred submittal.  Handrail contractor will provide an actual size shop drawing with dimensions to City for approval prior to installation.”

PC2. No further comment.  Deferred submittal.  Notate deferred submittals on cover sheet.

PC3. No further comment.

STRUCTURAL

APPLICABLE THROUGHOUT

- All final engineering plans, specifications, reports, and documents must include the date of signing below or next to the signature and seal. [B&P §6735]

PC2. No further comment.

- The site plan is not to stated scale and there are disagreeing set back dimensions on the west side of the property (ADU called out as being 4’ from property line but shown at same set back as garage and main dwelling listed at 3’).

PC2. No further comment.

- There is disagreement within the plans between #1 and #2 DF being used for joists. Spans were evaluated as #1 where notes for the members on the plan view. If utilizing #1 throughout please revise the general notes to reflect. All lumber grades will field verified.

PC2. No further comment.

- Provide the geotechnical analysis report referenced in the structural drawing foundation notes for review.

PC2. Not addressed, response indicates reference removed from plans however note remains.

PC3. The second note under the foundations section on sheet S0.1 indicates that the foundation work shall conform to the geo-technical report listed. Please provide the geo-technical report listed for review, or if no geo-technical analysis was conducted please remove the note.

- General note #6 indicates a maximum joist notch not to exceed D/5 which exceeds the allowable per R502.8. Please revise or provide calculations/justification for the design beyond the allowable prescriptive.

PC2. No further comment.

- General note 13 indicates all nailing to comply with the 1997 UBC. Please revised/update general notes to indicate compliance with the current CBC/CRC requirements.

PC2. Reference to the 1997 UBC still shown on sheet S0.3 note 13.

PC3. No further comment.

- The seismic design calculations utilize seismic coefficients from ASCE 7-16 which has not yet been adopted as a reference standard into the CBC/CRC. Please provide revised calculation utilizing the applicable coefficients from ASCE 7-10 as the values differ.

PC2. No further comment.

- The submitted shear wall design calculation information does not appear to correspond with plans in regards to shear wall lengths, shear wall type and hold downs etc. There also appears to be left over input values in the calculations that haven’t been carried through. Please review, revise, and resubmit.

PC2.  No further comment.

- Provide more accurate descriptions of the individual beam/joist calculations submitted or provide other suitable means for identification (i.e. # designation with mark-up) in order to match these members to their location on the plan. Please ensure calculations for all designed members are provided.

PC2. No further comment.

- Provide sections, details, or other clarification identifying how interior support in the crawlspace will be provided (i.e. pier/girder system, cripple wall, poured stem wall etc.).

PC2. Not addressed, revised exterior section detail provided for stem wall and new interior girder details provided for the new crawlspace beam #1 location, however the majority of the interior foundation supports still have not been identified or detailed.

PC3. No further comment.

- Clarify the spacing of the A35 connectors used to connect the rim to the cripple wall top plate in detail 1/S1.03. The detail references the schedule for space however the spacing information appears to have been omitted.

PC2. Not fully addressed, clarify the spacing of the A35 connectors in detail 1/S1.03 reference to schedule for spacing still existing in revised detail.

PC3. No further comment.

- Provide hold down installation details for the 1st floor hold downs at the cripple wall condition shown in detail 1/S1.03. Provide hold down installation details for the 1st floor hold downs at interior locations. Provide hold down

PC2. Not fully addressed, hold down detail provided for slab on grade condition however this is not applicable for the ADU or main dwelling. Provide hold down installation details for hold downs at the exterior stem walls as shown in detail 1/S1.03. Provide hold down installation details for interior hold down locations including specifics details for interior locations that are not shown at interior foundations.

PC3. Response indicates that detail 4/S.05 is applicable to all interior and exterior 1st floor hold downs. This detail is for a wall supported on a slab on grade condition which does not match the main dwelling or ADU construction. Please provide appropriate hold down detail. Please also provide the requested hold down detail for the interior shear wall locations that are not located above interior foundation walls (see SW-A at the 1st floor hall wall adjacent to bedroom #2 closet)

- Identify the shear capacity of shear wall A in the schedule as this information has been omitted.

PC2. No further comment.

- Provide complete exterior deck/porch construction details to include; joist to beam connection/bearing condition (flush vs drop), beam to column connections, ledger connection details where required, lateral load connection details, guard and knee wall construction & connection details. [R507]

PC2. Not addressed, details as noted above for exterior deck/porch construction have not been provided.

PC3. Per response deck details provided in 2 & 4/S0.6, however these details do not address all of the items in the original comment. Please provide ledger connection details, lateral load connection detail, guard and knee wall construction & connection details.

- Provide connection details showing how the upper level columns used to support the 2nd floor balcony and/or porch roof will be connected to the lower level columns to maintain a continuous load path.

PC2. The HUS410 hanger specified in the new detail 4/S0.6 exceeds the width of the post it is shown mounted to. Please revise.

PC3. No further comment.

- Clarify detail 15/S0.5 note 1.

PC2. No further comment.

- The crawlspace access detail 2/S0.5 doesn’t appear to be applicable with the cripple wall detail shown in 1/S0.3 please clarify.

PC2. No further comment.

- Clarify the typical note of “all posts and king post shall be 4x the width of the beam”. Is a 4x member with the same width as the beam to be used for the jack and king posts, are jack and kings that equal 4 times the beam width to be utilized?

PC2. No further comment.

- Please specify on the drawings that fasteners for pressure preservative-treated wood shall be of hot dipped zinc-coated galvanized steel, stainless steel, silicon bronze, or copper. [R317.3.1]

PC2. No further comment.

- Please submit a completed Special Inspection Agreement Form for all items subject to special inspections. All signatures and information must be provided prior to permit issuance. (https://www.ci.tracy.ca.us/documents/?d=Special_Inspection_Agreement.pdf)

PC2. Not yet provided, per response will be submitted prior to permitting.

- Provide engineered roof truss layout and calculations or include in a list of deferred submittal items on the cover sheet.

PC2. For Calculations:

  - Beam BM2 indicates a total deflection exceeding the L/360 maximum for floors per table R301.7, please revise accordingly.

PC3. Beam BM2 located at the 2nd floor level above the kitchen/dining area still exceeds the allowable deflection. Please revise.

  - There is a disagreement in the plans and calculations in regards to concrete compressive strength. The calculations reference a minimum Fc of 2500psi however the plans indicate 3000psi minimum, please clarify the disagreement. If concrete with a compressive strength exceeding 2500psi is used for the foundation it will need to be included in the special inspections.

PC3. No further comment.

  - ACI-318-83 version referenced in the structural design assumptions is outdated. Please revise to the 2014 version currently referenced in the 2016 CBC/CRC.

PC3. No further comment.

MAIN DWELLING SPECIFIC

- Clarify what portions of the existing main dwelling are existing to remain and what will be reconstructed as part of this project. Provide details for the connections/ties of the new to existing footings (i.e. dowel size, length, embedment, epoxy etc.). Provide details showing the connection of new to existing walls (i.e. strapping type, locations etc.)

PC2. Response is as provide remains unclear. Response: “The framing will follow the standard in new construction, but existing studs and floor framing will be used as new lumber per structural plans”. Will the main dwelling be reconstructed complete? Is lumber from demolition proposed to be reused? Are portions of the existing foundation to remain and be incorporated? Please clarify and provide an accurate scope of work and delineate any existing portions of the structure to remain from newly constructed work.

PC3. Since the main dwelling will be reconstructed completely, please revise the scope of work to reflect the actual proposed work. Currently the scope details a remodel of the existing 1st level with 1st level lateral additions and a 2nd story addition. Please also take note since the dwelling is to be reconstructed complete full compliance with the CRC including the required installation of residential fire sprinkler systems in both the main dwelling and the proposed ADU in accordance with CRC R313.2. Please provide the necessary fire sprinkler plans and supporting documents or indicate that they will be provided for both structures as a deferred submittal.

- Several portions of the 1st and 2nd floor system appear to be undersized/over spanned. Per CRC table R502.3.1(2) the maximum allowable clear span for #1 DF joist (40psf LL) is 16’5”. Please revise accordingly or provide calculations to validate, ensure the calculations are based on the actual clear spans and the required loading based on room usage.

PC2. No further comment.

- Identify the spacing of the lower level front porch/deck joists, ensure the actual joist spans comply for the spacing indicated per CRC table R507.5 or provide calculations to validate spans exceeding the allowable tabular.

PC2. No further comment.

- The 2 interior and plan right side 4x6 front porch/deck girders appear to be undersized/over spanned based on their clear span and the tributary load imposed. Please revise accordingly or provide calculation to validate. [R507.6]

PC2. Deck girders revised to 4x10 and deck joist direction revised. 1st level plan right 4x10 exceeds the allowable span per table R507.6; calculations were provided for this member however deflection exceeds L/360 as required for floors in table R301.7. Please revise accordingly.

PC3. No further comment.

- The 5” thick rear entry slab is noted as being at the 1st floor finished floor elevation. If the slab will be elevated above grade to match the FFE provide foundation/support details for the elevated slab. Alternatively, if the 5” slab is to be located at grade, provide construction details for the required elevated portion of the rear entry stoop.

PC2. Not fully addressed, typical slab on grade detail provided however slab is still noted at the 1st floor finished floor elevation and an elevated rear porch is shown on the architectural plans.

PC3. Not addressed, response indicates that the slab will be supported on compacted soil however the slab is indicated at the first floor finished floor elevation (see sheet S.01) which is located 2’4” above grade per the architectural plans. If the rear slab will be elevated above grade provide footing and stem wall details, if the slab will be at grade provide construction details for the required elevated rear entry porch as depicted on the architectural plans.

- Identify the required beam used to support the plan left side of the front entry roof cover.

PC2. Not addressed, response indicated that beam with match the opposite side of the roof system however neither beam size is indicated in resubmittal.

PC3. Not address. Identify the beams that will span from the outer columns to the front wall of the dwelling to carry the entry roof cover.

- Clarify how the roof truss bearing wall shown between bedroom #3 and the hallway will be supported continuous to the foundation as this wall location is not located at a crawlspace bearing location. If using the 1st floor system to support the bearing wall provide joist calculations that include the linear load from the bearing wall system to validate. If this wall will not be utilized for bearing, remove the hatch mark. This wall is also shown as a shear wall, provide details how the loading from the shear wall will be transferred to the foundation.

PC2. Not fully addressed, several notes indicate roof trusses to be designed to clear span the structure however interior bearing walls (as hatched per legend) are still depicted on the 2nd floor plan view  Calculation #1 on sheet 8 for the 2nd level exterior wall headers also indicates an assumed middle bearing wall. Please clarify.

PC3. Not fully addressed. Legend on sheet S.02 identifies hatched walls as “Bearing walls for trusses”. Interior 2nd floor walls shown hatched signifying bearing walls for trusses. Calculation #1 on sheet 8 for 2nd level exterior wall headers still indicates that calculation is “Assuming middle bearing wall”. If trusses will be designed to clear span and interior walls will not be utilized to support the trusses mid-span remove the bearing wall designation from the plan view on sheet S.02 and revise calculation 1 on page 8 to remove the assumption of the middle bearing wall.

- Provide typical detailing for the stair framing. Call out detail sections from plans. Ensure details include attachments at floors and intermediate landings.

PC2. No further comment.

6 2 CAR GARAGE SPECIFIC

- Clarify if the existing garage will be incorporated into the new structure or removed complete.

PC2. Per response existing 2 car garage is to be replaced per revised plan, the architectural plan depicts a new 2 car garage however the structural plans show a new 20x20 open carport. Please coordinate plans.

PC3. No further comment.

- Provide a complete calculation packet for the garage for review to include the garage door headers, ridge beams, and shear wall design calculations.

PC2. Response indicates that no calculations were provided as the revised garage framing is standard. Revised garage plans were not provided, however a 20 x 20 carport design was provided. The majority of the framing as shown on sheet S for the carport exceeds the prescriptive limits of the CRC and as such calculations are required. Additional comments may be forthcoming upon review or the carport calculations or a revised garage design.

PC3. Provide complete construction details for the garage. A foundation section and plan view were provided as well as a roof plan veiw and a ridge beam section, however not wall construction details or sections were provided. Please provide complete plans to include wall framing size/spacing, shear wall designations or prescriptive braced wall plans and details, wall to foundation anchorage, roof to wall connections, etc.

- Provide a detail for the ST6236 strap installation at the garage door openings and identify the # king studs adjacent to these openings as the clear opening exceeds table R602.7.5.

PC2. No further comment at this time.

ACCESSORY DWELLING UNIT

- Clarify if the existing garage will be incorporated into the new structure or removed complete.

PC2. No further comment.

- Provide a detail for the installation of the CS6236 strap(s) as shown on the roof plan.

PC2. No further comment.

- Clarify how the tie down straps are to be installed at the ADU roof level. The plan view references 16/S0.5 however this detail doesn’t appear applicable to this condition.

PC2. No further comment.

PC2. Additional structural comments:

103. Revised calculations for the ADU structure were not included in the resubmittal please provide. Please ensure the revised calculation reflect the changed dimensions of the structure.

PC3. The revised seismic design calculations for the ADU utilize seismic coefficients from ASCE 7-16 which has not yet been adopted as a reference standard into the CBC/CRC. Please provide revised calculation utilizing the applicable coefficients from ASCE 7-10 as the values differ.

104. The detail referenced for the interior hold down location in the ADU 16/S.05 depicts a 2nd level wall to the 1st floor wall condition hold down. Please provide a revised detail to reflect the hold down condition at this location.

PC3. No further comment

MECHANICAL

Sheet A.05

- Clarify and indicate that the central heating furnace system for the first floor will be provided with requirements appropriate clearance and installation as per CMC 906.

PC2. Provide section at stairway to show configuration of Furnace, venting for combustion air, and proximity to stairway windows and air conditioning unit.

PC3. No further comment.

- Indicate location of air conditioning unit.  Provide a note that the condensing unit shall rest on a concrete or other approved base extending not less than 3 inches above the adjoining ground level as per CMC 1105.2.

PC2. No further comment.

Sheet A.06/A.09

- Where a closet is designed for the installation of a clothes dryer, an opening of not less than 100 sq. in. for makeup air shall be provided in the door or by other approved means as per CMC 504.4.1(1).

PC2. Applicant indicates on the ADU that a water heater is to be placed in the closet.  Provide manufacturer’s specifications to confirm that the closet provides sufficient clearances and combustion air as per manufacturer’s instructions.

PC3. No further comment.

PLUMBING

General

- For the proposed dwelling and accessory dwelling unit, provide a diagram of the gas line piping from the meter to appliances.  Indicate the gas input required by each appliance, pipe sizes, and distances in order to verify adequate pipe sizing.

PC2. Note the following:

  - For Main dwelling gas line sizing, the sizing does not match the required per Table 1319.2(1).  With the longest remote gas outlet being 84 feet from the meter to the furnace under the staircase, the length used on the table should be 90 feet.  With the full gas demand of 375,000 BTU/H or 340.9 cfh for the system, the system’s main branches would need to be upsized based on their capacity.  See CPC Figure 1216.1.1 for example of sizing each section and outlet of the piping system.

PC3. No further comment.

  - For ADU gas line sizing, gas line calculation for sizing needs to take into account the distance from the gas meter on the existing residence to the ADU as shown on Sheet A.02.  This is scaled out to be approximately 169 feet.  Thus, the furthest gas outlet for your ADU is the stove and oven, which would be 198 feet.  Thus, the sizing of the gas line for the ADU should use Table 1319.2(1), the 200 ft length, and max gas demand of 280,000 BTU/H or about 254 cfh.  This requires a larger main branch from the gas meter on the existing residence to the ADU.  And all of the subsequent system for the ADU need to be resized unless a separate meter will be run to the ADU.  See CPC Figure 1216.1.1 for example of sizing each section and outlet of the piping system.

PC3. No further comment.

Sheet A.05

- The proposed 1St Floor Plan indicates that the direct vent water heater will be in a closet by the kitchen.  Clarify and indicate on plans how you will provide air for combustion and ventilation as per CPC 506 and manufacturer’s specifications.

PC2. Provide specifications for water heater to confirm that the closet provides sufficient clearances and combustion air as per manufacturer’s instructions.

PC3. No further comment.

- The proposed 1st and 2nd floor plan indicates that the addition will bring the total amount of water closets to 4.  According to note 4 on CPC Table 703.2, with 4 water closets, the drainage piping needs to be upgraded to a 4” pipe.  Indicate that the sewer drainage line will be upgraded to meet maximum unit loading per CPC Table 703.2.

PC2. No further comment.

ELECTRICAL

Sheet A.05/A.06

- The first floor indicates that the Electrical Panel on the outside is only a 100 amp Panel.  The subpanel on the inside of the first floor is also indicated on the legend as a 100 amp Panel.  The subpanel on the inside of the second floor is also indicated on the legend as a 100 amp Panel.  Please provide an electrical load calculation that the 100 amp main panel is adequate for the expected electrical load.

PC2. Provide electrical load calculation for Main residence, new 2-car garage, and new ADU.  Clarify if PG&E will be providing a separate service for ADU.  Floor plan on Sheet A.05 still indicates that main panel for existing residence is only a 100 A panel.

PC3. No further comment.

- Per CEC 250.52(E)(1), an outdoor receptacle shall be installed at the front and back of the dwelling.  Provide outdoor receptacle for back of dwelling.

PC2. No further comment.

- Provide weather-resistant type receptacles and provide a waterproof enclosure for outdoor receptacles as per CEC 406.9(A).  Balcony and outdoor receptacles are only indicated as GFCI.

PC2. No further comment.

- Provide at least one receptacle outlets at each peninsular countertop space with a long dimension of 2 feet or greater and a short dimension of 1 foot or great.

PC2. No further comment.

Sheet A.09

- The floor plan for the ADU indicates an 100 amp Electrical Panel on the outside with a subpanel on the inside of the ADU behind a door.  Please indicate if this will be a separate PG&E panel or if this will be part of main service from existing dwelling.  If this is proposed to be an extension of the existing electrical service at the existing dwelling, provide electrical load calculation, and site plan details on how utilities will be run.

PC2. Change swing of main entrance door so that electrical subpanel on ADU can be serviced and will not be located in an area where it will be exposed to physical damage as per CEC 240.24(C).

PC3. No further comment.

Sheet A.10

- Verify window type and sizes from floor plan with elevations.

PC2. No further comment.

Sheet A.11

- The 6 car garage proposes electrical at the garage.  Indicate how electrical will be run to the 6 car garage.  Will there be a separate panel?

PC2.  Provide electrical load calculation for main panel, 2 car garage, and new ADU.  Indicate size of wire and conduit size.

ENERGY

Sheet A.14

- Energy Calculations are provided for the 1 story accessory dwelling unit.  However, per CEnC Section 100.0E.3.B, the Energy Code requirements apply to additions and alterations to existing buildings.  Provide energy analysis for addition to existing building since project proposes to add habitable space on both the 1st and 2nd floors.

PC2.  The resubmitted energy calculations are only for the new ADU.

  - Provide energy analysis for addition and remodel to Existing Residence.

PC3. Submitted energy analysis for the primary dwelling does not reflect the proposed construction. The calculations indicate a total conditioned area of 1735 square feet, duct work located outside of the attic space, window overhangs, and a cool roof system. Please provide revised energy calculations that accurately depict the proposed newly constructed 2 story dwelling and the appropriately installed features.

Sheet A.05/A.06/A.09

- In bathrooms, garages, laundry rooms, and utility rooms, at least one luminaire in each of these spaces shall be controlled by a vacancy sensor.  Indicate the proposed switches in floor plans.

PC2. No further comment.

- Lighting required to comply with Reference Joint Appendix JA8 per CEnC Table 150.0-A shall be controlled by dimmers or vacancy sensors as per CEnC 150.0(k)2K.  Indicate this on plans.

PC2. No further comment.

- Provide the mandatory water heating system requirements of CEnC §150.0(n)1:

    - A 120V electrical receptacle that is within 3 feet from the water heater and accessible to the water heater with no obstructions; and

    - A Category III or IV vent, or a Type B vent with straight pipe between the outside termination and the space where the water heater is installed; and

    - A condensate drain that is no more than 2 inches higher than the base of the installed water heater, and allows natural draining without pump assistance; and

    - A gas supply line with a capacity of at least 200,000 Btu/hr.

PC2. No further comment.

Energy Calculations

- Match Azimuth locations of openings with azimuth of ADU with floor plan and elevations.  According to Floor Plan, the North is the back of the ADU.  However, per the elevation, the NorthEast is the back of the ADU.  And per the Energy Calculations, the rear wall is South (180 degrees azimuth).

PC2. No further comment.

- The glazing specified on the ADU residential calculations do not match with the windows on the ADU floor plan.  Revise Calculations since Fenestration indicates 12 windows and floor plan only indicates 10 windows.

PC2. No further comment.

- HERS features indicates that ducts are located entirely in conditioned space.  Clarify.

PC3. Comment has not been addressed, HERS features for the ADU indicate cool roof, window overhangs, and ducts located within conditioned space all of which are not detailed in the plans.

- Calculations indicate door located on front wall.  However, door is located on south-east elevation.

PC2. No further comment.

GREEN BUILDING STANDARDS

Sheet A.15

- Please update the Mandatory Measures to City of Tracy 2016 CalGreen Residential Mandatory Measures Checklist with July 1, 2018 updates (see attached).  Current provided form is outdated.

PC2. Comment till Outstanding.  Current form is outdated.

PC3. Please see attached City of Tracy CalGreen checklist for inclusion in resubmittal.

- END -

cc: permit file